## Sheet1
cmd | comment | data1 | data2 | data3 | data4 | data5 | data6 | data7 | data8
A0 | cmd | 0x1a: swing up/down |  | bit 4:0 temp | mode | 0xf4: on |  | bit 5: quiet
|  | 0x1f: off |  | bit 5: auto fan | 0: auto | 0xc4: off
|  | bit 5: sleep |  | bit 7:6 fan speed | 1: cool
2: dry
3: fan
4: heat
50 | reply of a0
53 | reply | 0 | 0 | 0 | 0 | 0x1a: swing up/down | 0 | 0 | mode
0: no swing
54 | reply | 0x21 | 0: swing up/down | 0x1e | 0 | 0 | 1: idle (off) | 0 | 0
|  |  | 0x11 - 0x15: blade position when no swing |  |  |  | 0: working
not correct ??
52 | reply | bit 4-0: set temp - 9 | bit 4-0: measured temp - 9 | temp? | 0xF8: no swing | bit 3-0: 1=wired, 2=remote |  |  | temp?
[5 empty] | 0xd0: swing up/down | bit 8: airco on
64 | set | data1: 0x20; data2: 0 : use internal unit temp; data3: data3 + data4: wired remote room temp; data6: temp ?
1: use wired remote temp
| reply | 0x20 | 0 : use internal unit temp | data3 + data4: used temp |  | data5 + data6: own temp |  | 0 | 0
1: use wired remote temp
63 | cmd | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| reply | data1: 0; data2: 0
70 | cmd (error code) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
reply
71 | cmd | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| reply | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
83 | cmd | 0 | 0xff | 0xff | 0xff | 0xff | 0xff | 0xff | 0xff
noreply
d1 | cmd | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
noreply